## Info
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B)
Click here to download the EPA-NR report
At some parts the calculation method in this spreadsheet is simplified compared to EPA-NR. These simplifications are mentioned in the calculation sheets in comment boxes.
This excel file contains the following worksheets:
| Input & Results sheet: | Input & Results | contains all input parameters and calculation results
| Calculation sheets: | Calculation Q_Heating | calculates the energy need, delivered energy and primary energy use for space heating
|  | Calculation Q_Cooling | calculates the energy need, delivered energy and primary energy use for space cooling
|  | Calculation Q_DHW | calculates the primary energy use for domestic hot water (DHW)
|  | Calculation Q_Fans | calculates the primary energy use for fans
|  | CSI reference heating | calculates the reference energy use for heating for the Climate Severity Index (reference climate is Brussels)
|  | CSI reference cooling | calculates the reference energy use for cooling for the Climate Severity Index (reference climate is Brussels)
| Climate sheets: | contain the climate data used in the calculation (16 climates sheets for specific countries and 3 empty climate sheets)

## Input & Results
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B). See Info sheet for details.
Click here to download the EPA-NR report
To see all worksheets in this spreadsheet click the "Unhide sheets" button.
See the Info sheet for details.
To hide all unnecessary worksheets click the "Hide sheets" button.
| Necessary input parameters |  |  |  | Calculation results
Annual energy use
[6 empty] | climate |  | BE - Brussels
|  | Climate (not included when default buttons are pressed) | 1 |  |  | Qprim,H | 33694.412 | MJ
|  | choose climate* | 3 |  |  | Qprim,C | 0 | MJ
|  | * for information about how to use your own climate data see the comment box |  |  |  | Qprim,DHW | 17597.04 | MJ
[6 empty] | Qprim,Fans | 4173.6038 | MJ
|  | U-value building elements (not included when default buttons are pressed) |  |  |  | Qprim,tot | 55465.0559 | MJ
|  | U-value opaque facade | 0.44 | W/m2K
|  | U-value opaque roof | 0.23 | W/m2K |  | Climate Severity Index (CSI)
|  | U-value floor | 0.21 | W/m2K |  | climate |  | BE - Brussels
|  | U-value doors | 3 | W/m2K |  | QCSI,tot,Brussels | 12597.0641 | W
|  | U-value windows (incl. glazing, frames, spacer) | 1.71 | W/m2K |  | CSI heating | 1 | -
[6 empty] | CSI cooling | 0 | -
|  | Geometry |  |  |  | CSI total | 1 | -
|  | total usable area | 129.39 | m2
|  | floor area | 43.13 | m2
|  | roof area (opaque) | 43.13 | m2
|  | east facade - opaque wall area | 66.5 | m2
|  | east facade - window area | 1.5 | m2
|  | east facade - door area | 0 | m2
|  | south facade - opaque wall area | 34 | m2
|  | south facade - window area | 9.75 | m2
|  | south facade - door area | 2.2 | m2
|  | west facade - opaque wall area | 0 | m2
|  | west facade - window area | 0 | m2
|  | west facade - door area | 0 | m2
|  | north facade - opaque wall area | 35.7 | m2
|  | north facade - window area | 8 | m2
|  | north facade - door area | 2.2 | m2
|  | Ventilation system | 2
|  | ventilation type | 2
|  | heat recovery efficiency (ηhru) (bypassed in summer) | 0
|  | Heating system | 1
|  | total heating system efficiency (ηH) | 0.9
|  | energy type | 1
|  | Cooling system | 2
|  | total cooling system efficiency (ηC) | 0
|  | energy type | 2
Domestic hot water (DHW) system
|  | total DHW system efficiency (ηDHW) | 0.5
|  | reduction DHW need | 0 | %
|  | energy type | 1
Default and fixed values (press button for default values)
Indoor conditions
|  | indoor setpoint temperature for heating (θi,H) | 19 | °C
|  | indoor setpoint temperature for cooling (θi,C) | 24 | °C
|  | internal heat sources (Φi) per m2 | 6 | W/m2
Ventilation
|  | air flow rate (infiltration and ventilation) per m2 | 0.6 | dm3/(s·m2)
|  | mechanical fraction of total air flow rate | 0.6 | -
Window properties
|  | g-value glazing (gg) | 0.72 | -
|  | glazing fraction (fgl) | 0.75 | -
2
Shading devices
|  | shading reduction factor movable shading device cooling (Fsh,g,C) | 1 | -
Opaque building element properties
|  | absorption coefficient for solar radiation (αS,c) | 0.8 | -
|  | external surface heat resistance (Rse) | 0.04 | m2K/W
|  | emissivity for thermal radiation of the external surface (ε) | 0.9 | -
Form factors
|  | form factor, unshaded horizontal roof (Fr,k) | 1 | -
|  | form factor, unshaded vertical wall (Fr,k) | 0.5 | -
Air and sky temperature
|  | average difference between external air and sky temperature (Δθer) | 11 | K
Dynamic parameters
|  | a0,H | 1 | -
|  | τ0,H | 15 | h
|  | a0,C | 1 | -
|  | τ0,C | 15 | h
|  | building mass per m2 (Cm/m2) | 370000 | J/Km2
Transmission losses
|  | loss coefficient floor (btr,floor) | 0.75 | -
|  | thermal bridges | 0 | W/K
Fans
|  | energy use in case of natural ventilation | 0 | kWh/m2
|  | energy use in case of mechanical exhaust | 3.5 | kWh/m2
|  | energy use in case of mechanical supply and exhaust | 6.6 | kWh/m2
DHW
|  | DHW need | 68 | MJ/m2
Energy conversion factor
|  | gas | 1 | -
|  | electricity | 2.56 | -
Climate severity index constants
|  | a1 | 300 | -
|  | a2 | 5 | -
|  | b1 | 12 | -
|  | b2 | 0.02 | -
|  | c | 800 | -
Lists for list boxes
|  | Climate worksheets | Ventilation type |  |  | Energy type
|  | NL - De Bilt | natural supply and exhaust |  |  | gas
|  | DE - Berlin | nat. supply, mech. exhaust |  |  | electricity
|  | BE - Brussels | mech. supply and exhaust |  |  | other
|  | FR - Paris | mech. sup. and exh. + heat recovery
DK - Kobenhavn
CZ - Praha
ES - Madrid
PL - Warszawa
FI - Helsinki
IT - Rome
NO - Oslo
RO - Bucharest
HU - Budapest
IE - Dublin
GB - London
LT - Vilnius
Climate 1
Climate 2
Climate 3
Note on D96: - sub-polar areas: 9K - intermediate zones: 11K - tropics: 13K
Note on C77: This value is only used when mechanical ventilation is present.
Note on C80: This value can be derived from the perpendicular g-value and a correction factor: g-value = g-value perpendicular * Fw Default values: g-value perpendicular = 0.8 Fw = 0.9
Note on C81: This fraction is derived from the frame area fraction (Ff): Fgl = 1-Ff Default values: Ff = 0.25
Note on C83: The shading device is only used for the calculation of Qcooling.
Note on C119: The default value is based on an efficiency of 39% (1/0.39).
Note on C111: The default value is based on air conditioning (AC).
Note on C112: The default value is based on air conditioning (AC).
Note on C18: If you would like to use your own set of monthly climate data you must select Climate 1, 2 or 3 in the listbox. After selecting one of these options a climate sheet with the same name will appear after the input sheet (on the bottom of this page). You can enter your own monthly climate data in this sheet. This data sheet will be used for the calculation.
Note on C57: Enter the value for the energy conversion factor for "other energy type" in the next cell.
Note on C56: Gas en electricity For gas and electricity the energy conversion factor has a default value. This value can be changed in the fixed values and constants box below. Other energy type If another energy type is used, it is possible to enter your own energy conversion factor by selecting "other" in the list box and entering a value for the energy conversion factor.
Note on C62: Gas en electricity For gas and electricity the energy conversion factor has a default value. This value can be changed in the fixed values and constants box below. Other energy type If another energy type is used, it is possible to enter your own energy conversion factor by selecting "other" in the list box and entering a value for the energy conversion factor.
Note on C51: Gas en electricity For gas and electricity the energy conversion factor has a default value. This value can be changed in the fixed values and constants box below. Other energy type If another energy type is used, it is possible to enter your own energy conversion factor by selecting "other" in the list box and entering a value for the energy conversion factor.
Note on C52: Enter the value for the energy conversion factor for "other energy type" in the next cell.
Note on C63: Enter the value for the energy conversion factor for "other energy type" in the next cell.
Note on C61: This factor (%) takes into account the reduction of the DHW need by a solar collector, shower water heat recovery etc.
Note on C84: This shading reduction factor can be calculated according to formula 45 in EPA-NR (§6.6.2).

## Calculation Q_Heating (hidden)
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B). See Info sheet.
Click here to download the EPA-NR report
The paragraph numbers mentioned in this worksheet refer to the paragraphs in the EPA-NR report.
Calculation energy use heating (Qprim,H)
| Month |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Length of month | Ms | 2.6784 | 2.4192 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784
Heat transfer by transmission (§6.2)
| HT | W/K | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584
| QT | MJ | 5426.4161 | 4690.956 | 4370.645 | 3277.0888 | 2070.9731 | 1112.3824 | 590.6396 | 657.5479 | 1464.2472 | 2827.2481 | 4135.5823 | 5129.3507
Heat transfer by ventilation (§6.3)
| HV;adj | W/K | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608
| QV | MJ | 4118.0837 | 3559.9462 | 3316.8636 | 2486.9685 | 1571.6525 | 844.1822 | 448.2339 | 499.0102 | 1111.2108 | 2145.5864 | 3138.4756 | 3892.642
Internal heat sources (§6.4)
| Qi | MJ | 2079.3491 | 1878.1217 | 2079.3491 | 2012.2733 | 2079.3491 | 2012.2733 | 2079.3491 | 2079.3491 | 2012.2733 | 2079.3491 | 2012.2733 | 2079.3491
Solar heat sources (§6.5 and §6.6)
| Φsol,mn,east,window | W | 12.5979 | 27.1493 | 43.9362 | 64.1513 | 89.6967 | 91.0569 | 89.1246 | 73.8829 | 54.8888 | 35.463 | 14.9856 | 9.3726
| Φsol,mn,south,window | W | 212.8276 | 364.3471 | 444.795 | 525.3627 | 541.5186 | 502.438 | 519.3924 | 538.0117 | 524.0667 | 453.9651 | 261.8425 | 196.4885
| Φsol,mn,west,window | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,window | W | 32.2391 | 71.3586 | 120.2003 | 192.0985 | 275.4971 | 289.8835 | 291.6052 | 234.6197 | 152.3968 | 90.352 | 42.1768 | 21.2278
| Φsol,mn,east,wall | W | -11.4694 | 5.3512 | 24.756 | 48.1237 | 77.653 | 79.2252 | 76.9916 | 59.373 | 37.4167 | 14.9614 | -8.7094 | -15.1977
| Φsol,mn,south,wall | W | 6.0417 | 19.8186 | 27.1334 | 34.459 | 35.928 | 32.3745 | 33.9161 | 35.6091 | 34.3411 | 27.9672 | 10.4984 | 4.5561
| Φsol,mn,west,wall | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,wall | W | -10.2239 | -5.6721 | 0.010885 | 8.3766 | 18.0805 | 19.7545 | 19.9548 | 13.3242 | 3.7571 | -3.4621 | -9.0676 | -11.5051
| Φsol,mn,east,door | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,south,door | W | 2.6655 | 8.7435 | 11.9706 | 15.2025 | 15.8506 | 14.2829 | 14.963 | 15.7099 | 15.1505 | 12.3385 | 4.6317 | 2.01
| Φsol,mn,west,door | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,door | W | -4.2958 | -2.3832 | 0.0045735 | 3.5196 | 7.5969 | 8.3002 | 8.3844 | 5.5984 | 1.5786 | -1.4547 | -3.8099 | -4.8341
| Φsol,mn,roof | W | -11.0707 | -2.1826 | 8.611 | 25.4347 | 40.0372 | 42.5772 | 40.9892 | 33.0514 | 17.4987 | 3.2129 | -8.8493 | -12.9752
| Qsol | MJ | 614.1893 | 1177.0139 | 1825.1098 | 2376.1603 | 2951.2177 | 2799.0823 | 2933.7082 | 2702.9886 | 2180.1184 | 1696.3463 | 787.1875 | 506.6005
Total heat transfer and heat sources (§6.1.3)
| QL,H | MJ | 9544.4998 | 8250.9022 | 7687.5086 | 5764.0574 | 3642.6256 | 1956.5646 | 1038.8735 | 1156.5581 | 2575.458 | 4972.8345 | 7274.0579 | 9021.9927
| QG,H | MJ | 2693.5383 | 3055.1357 | 3904.4589 | 4388.4336 | 5030.5668 | 4811.3556 | 5013.0572 | 4782.3377 | 4192.3917 | 3775.6953 | 2799.4607 | 2585.9495
Energy need for heating (§6.1.1)
| τ | h | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898
| aH | - | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106
| γH | - | 0.28221 | 0.37028 | 0.5079 | 0.76134 | 1.381 | 2.4591 | 4.8255 | 4.135 | 1.6278 | 0.75926 | 0.38486 | 0.28663
| ηG,H | - | 0.99888 | 0.99605 | 0.98427 | 0.92685 | 0.67945 | 0.40421 | 0.20718 | 0.24171 | 0.59357 | 0.92752 | 0.99529 | 0.99879
| QNH | MJ | 6853.9893 | 5207.8475 | 3844.4689 | 1696.6395 | 224.6164 | 11.7844 | 0.26644 | 0.62417 | 86.9708 | 1470.817 | 4487.7756 | 6439.1709
Annual energy use for heating (§6.9.2) | bar: Jan
| QNH | MJ | Jan: 30324.9708
| Qgen,H | MJ | Jan: 33694.412
| Qprim,H | MJ primary | Jan: 33694.412
Calculation energy use climate severity index heating (QCSI,H)
Climate severity index variables
| qsol, average | W/m2 | 22.6656 | 40.9038 | 58.3058 | 79.3693 | 99.2527 | 97.9183 | 98.1748 | 89.5313 | 70.2003 | 51.422 | 27.1489 | 19.1469
| aH | - | 217.4805 | 221.0216 | 233.5356 | 248.5042 | 268.5067 | 282.5201 | 291.0181 | 290.0007 | 276.991 | 257.006 | 235.0139 | 221.998
| bH | - | 11.5467 | 11.1819 | 10.8339 | 10.4126 | 10.0149 | 10.0416 | 10.0365 | 10.2094 | 10.596 | 10.9716 | 11.457 | 11.6171
| cH | - | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| QCSI,H | W | 2527.5637 | 2233.8038 | 1672.6818 | 932.9439 | 0 | 0 | 0 | 0 | 0 | 845.7613 | 1943.482 | 2440.8276
Energy use climate severity index heating (QCSI,H) | bar: Jan
| QCSI,H | W | Jan: 12597.0641
Note on C46: According to §6.8.3
Note on C47: According to §6.8.1
Note on C49: According to §6.8.1
Note on C48: According to §6.8.1

## Calculation Q_Cooling (hidden)
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B). See Info sheet.
Click here to download the EPA-NR report
The paragraph numbers mentioned in this worksheet refer to the paragraphs in the EPA-NR report.
Calculation energy use cooling (Qprim,C)
| Month |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Length of month | Ms | 2.6784 | 2.4192 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784
Heat transfer by transmission (§6.2)
| HT | W/K | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584 | 122.7584
| QT | MJ | 7070.3963 | 6175.8413 | 6014.6251 | 4868.0374 | 3714.9532 | 2703.3309 | 2234.6198 | 2301.528 | 3055.1957 | 4471.2283 | 5726.5309 | 6773.3308
Heat transfer by ventilation (§6.3)
| HV;adj | W/K | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608 | 93.1608
| QV | MJ | 5365.6932 | 4686.8192 | 4564.473 | 3694.3325 | 2819.2619 | 2051.5461 | 1695.8433 | 1746.6197 | 2318.5748 | 3393.1958 | 4345.8395 | 5140.2515
Internal heat sources (§6.4)
| Qi | MJ | 2079.3491 | 1878.1217 | 2079.3491 | 2012.2733 | 2079.3491 | 2012.2733 | 2079.3491 | 2079.3491 | 2012.2733 | 2079.3491 | 2012.2733 | 2079.3491
Solar heat sources (§6.5 and §6.6)
| Φsol,mn,east,window | W | 12.5979 | 27.1493 | 43.9362 | 64.1513 | 89.6967 | 91.0569 | 89.1246 | 73.8829 | 54.8888 | 35.463 | 14.9856 | 9.3726
| Φsol,mn,south,window | W | 212.8276 | 364.3471 | 444.795 | 525.3627 | 541.5186 | 502.438 | 519.3924 | 538.0117 | 524.0667 | 453.9651 | 261.8425 | 196.4885
| Φsol,mn,west,window | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,window | W | 32.2391 | 71.3586 | 120.2003 | 192.0985 | 275.4971 | 289.8835 | 291.6052 | 234.6197 | 152.3968 | 90.352 | 42.1768 | 21.2278
| Φsol,mn,east,wall | W | -11.4694 | 5.3512 | 24.756 | 48.1237 | 77.653 | 79.2252 | 76.9916 | 59.373 | 37.4167 | 14.9614 | -8.7094 | -15.1977
| Φsol,mn,south,wall | W | 6.0417 | 19.8186 | 27.1334 | 34.459 | 35.928 | 32.3745 | 33.9161 | 35.6091 | 34.3411 | 27.9672 | 10.4984 | 4.5561
| Φsol,mn,west,wall | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,wall | W | -10.2239 | -5.6721 | 0.010885 | 8.3766 | 18.0805 | 19.7545 | 19.9548 | 13.3242 | 3.7571 | -3.4621 | -9.0676 | -11.5051
| Φsol,mn,east,door | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,south,door | W | 2.6655 | 8.7435 | 11.9706 | 15.2025 | 15.8506 | 14.2829 | 14.963 | 15.7099 | 15.1505 | 12.3385 | 4.6317 | 2.01
| Φsol,mn,west,door | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Φsol,mn,north,door | W | -4.2958 | -2.3832 | 0.0045735 | 3.5196 | 7.5969 | 8.3002 | 8.3844 | 5.5984 | 1.5786 | -1.4547 | -3.8099 | -4.8341
| Φsol,mn,roof | W | -11.0707 | -2.1826 | 8.611 | 25.4347 | 40.0372 | 42.5772 | 40.9892 | 33.0514 | 17.4987 | 3.2129 | -8.8493 | -12.9752
| Qsol | MJ | 614.1893 | 1177.0139 | 1825.1098 | 2376.1603 | 2951.2177 | 2799.0823 | 2933.7082 | 2702.9886 | 2180.1184 | 1696.3463 | 787.1875 | 506.6005
Total heat transfer and heat sources (§6.1.3)
| QL,C | MJ | 12436.0894 | 10862.6605 | 10579.0982 | 8562.3699 | 6534.2152 | 4754.8771 | 3930.4631 | 4048.1477 | 5373.7705 | 7864.4241 | 10072.3704 | 11913.5823
| QG,C | MJ | 2693.5383 | 3055.1357 | 3904.4589 | 4388.4336 | 5030.5668 | 4811.3556 | 5013.0572 | 4782.3377 | 4192.3917 | 3775.6953 | 2799.4607 | 2585.9495
Energy need for cooling (§6.1.1)
| τ | h | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898 | 61.5898
| aC | - | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106 | 5.106
| γC | - | 0.21659 | 0.28125 | 0.36907 | 0.51253 | 0.76988 | 1.0119 | 1.2754 | 1.1814 | 0.78016 | 0.4801 | 0.27793 | 0.21706
| ηL,C | - | 0.21652 | 0.28094 | 0.36763 | 0.50415 | 0.71144 | 0.84112 | 0.9194 | 0.89735 | 0.71829 | 0.47414 | 0.27764 | 0.21699
| QNC | MJ | 0.85533 | 3.3797 | 15.2128 | 71.6917 | 381.8905 | 811.9182 | 1399.3968 | 1149.742 | 332.4694 | 46.8535 | 2.9282 | 0.82978
Annual energy use for cooling (§6.9.2) | bar: Jan
| QNC | MJ | Jan: 4217.168
| Qgen,H | MJ | Jan: 0
| Qprim,H | MJ primary | Jan: 0
Calculation energy use climate severity index cooling (QCSI,C)
Climate severity index variables
| qsol, average | W/m2 | 22.6656 | 40.9038 | 58.3058 | 79.3693 | 99.2527 | 97.9183 | 98.1748 | 89.5313 | 70.2003 | 51.422 | 27.1489 | 19.1469
| aC | - | 192.4805 | 196.0216 | 208.5356 | 223.5042 | 243.5067 | 257.5201 | 266.0181 | 265.0007 | 251.991 | 232.006 | 210.0139 | 196.998
| bC | - | 11.5467 | 11.1819 | 10.8339 | 10.4126 | 10.0149 | 10.0416 | 10.0365 | 10.2094 | 10.596 | 10.9716 | 11.457 | 11.6171
| cC | - | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| QCSI,C | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy use climate severity index cooling (QCSI,C) | bar: Jan
| QCSI,C | W | Jan: 0
Note on C46: According to §6.8.3
Note on C47: According to §6.8.2
Note on C49: According to §6.8.2
Note on C48: According to §6.8.2

## Calculation Q_DHW (hidden)
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B). See Info sheet.
Click here to download the EPA-NR report
The calculation of the energy use of domestic hot water (DHW) is a simplified calculation method. This method is not based on the calculation method in EPA-NR.
Calculation energy use domestic hot water (Qprim,DHW)
Annual energy use for domestic hot water
| Qdem,DHW | MJ | 8798.52
| Qgen,DHW | MJ | 17597.04
| Qprim,DHW | MJ primary | 17597.04
Note on C10: The calculation method is simplified compared to EPA-nr §6.9.5.

## Calculation Q_Fans (hidden)
This spreadsheet is based on the calculation method of EPA-NR (Functional specifications of the EPA-NR software, june 2007 - Report Number: 2007-D-R0292/B). See Info sheet.
Click here to download the EPA-NR report
The calculation of the energy use of fans is a simplified calculation method. This method is not based on the calculation method in EPA-NR.
Calculation energy use fans (Qprim,Fans)
Annual energy use for fans
| QFans | MJ | 1630.314
| Qprim,Fans | MJ primary | 4173.6038
Note on C10: The calculation method is simplified compared to EPA-nr.

## Climate data (hidden)
This sheet is used in the calculation sheets. Don't change anything in this sheet. If you want to use your own climate data in the calculation use the Climate 1, 2 and 3 sheets.
Climate data
| BE - Brussels |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 2.4961 | 3.2043 | 5.7071 | 8.7008 | 12.7013 | 15.504 | 17.2036 | 17.0001 | 14.3982 | 10.4012 | 6.0028 | 3.3996
| Solar radiation - East | W/m2 | 18.688 | 36.6526 | 57.3772 | 82.3341 | 113.8717 | 115.5509 | 113.1653 | 94.3485 | 70.8989 | 46.9164 | 21.6358 | 14.7062
| Solar radiation - South | W/m2 | 43.5581 | 72.3367 | 87.6165 | 102.919 | 105.9875 | 98.5648 | 101.785 | 105.3215 | 102.6728 | 89.3582 | 52.8677 | 40.4547
| Solar radiation - West | W/m2 | 17.8185 | 34.9727 | 57.2704 | 84.6219 | 110.2442 | 107.3198 | 107.1128 | 101.0103 | 68.8175 | 45.3636 | 21.1941 | 13.3778
| Solar radiation - North | W/m2 | 10.5977 | 19.6532 | 30.9592 | 47.6022 | 66.9075 | 70.2377 | 70.6362 | 57.4451 | 38.412 | 24.0498 | 12.8981 | 8.0488
| Solar radiation - Horizontal | W/m2 | 26.9997 | 54.9992 | 89.0016 | 142.0004 | 188.0014 | 196.0031 | 191.0006 | 165.9946 | 117 | 71.9963 | 33.9977 | 21.0002
| Time |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Time (Ms) | Ms | 2.6784 | 2.4192 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784 | 2.6784 | 2.592 | 2.6784 | 2.592 | 2.6784

## Climate 1 (hidden)
In this sheet you can fill in your own monthly climate data.
| <<TYPE HERE YOUR CLIMATE NAME>> |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C
| Solar radiation - East | W/m2
| Solar radiation - South | W/m2
| Solar radiation - West | W/m2
| Solar radiation - North | W/m2
| Solar radiation - Horizontal | W/m2

## Climate 2 (hidden)
In this sheet you can fill in your own monthly climate data.
| <<TYPE HERE YOUR CLIMATE NAME>> |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C
| Solar radiation - East | W/m2
| Solar radiation - South | W/m2
| Solar radiation - West | W/m2
| Solar radiation - North | W/m2
| Solar radiation - Horizontal | W/m2

## Climate 3 (hidden)
In this sheet you can fill in your own monthly climate data.
| <<TYPE HERE YOUR CLIMATE NAME>> |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C
| Solar radiation - East | W/m2
| Solar radiation - South | W/m2
| Solar radiation - West | W/m2
| Solar radiation - North | W/m2
| Solar radiation - Horizontal | W/m2

## NL - De Bilt (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| NL - De Bilt |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 2.5 | 2.7 | 5.6 | 8 | 12 | 15.5 | 17 | 16.4 | 13.8 | 11.2 | 5.9 | 3.4
| Solar radiation - East | W/m2 | 17.1744 | 30.1753 | 61.6039 | 92.2068 | 119.8477 | 136.1883 | 116.4875 | 118.7276 | 74.8457 | 42.5627 | 20.8333 | 14.5609
| Solar radiation - South | W/m2 | 39.9492 | 59.1104 | 102.6732 | 119.5988 | 120.221 | 123.8426 | 113.874 | 139.6356 | 107.6389 | 82.8853 | 50.5401 | 34.3489
| Solar radiation - West | W/m2 | 17.1744 | 30.1753 | 61.6039 | 92.2068 | 119.8477 | 136.1883 | 116.4875 | 118.7276 | 74.8457 | 42.5627 | 20.8333 | 14.5609
| Solar radiation - North | W/m2 | 11.5741 | 20.2546 | 36.2157 | 49.7685 | 70.5645 | 85.2623 | 72.8047 | 61.2306 | 42.4383 | 25.7616 | 13.5031 | 8.9606
| Solar radiation - Horizontal | W/m2 | 24.2682 | 46.2963 | 97.0729 | 144.6759 | 192.279 | 220.2932 | 193.0257 | 185.1852 | 113.8117 | 64.5908 | 30.0926 | 19.0412

## DE - Berlin (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| DE - Berlin |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -0.40148 | 0.60565 | 3.9999 | 8.4003 | 13.5 | 16.7001 | 17.8993 | 17.2013 | 13.5014 | 9.2988 | 4.6003 | 1.2
| Solar radiation - East | W/m2 | 16.9247 | 34.6532 | 63.2639 | 89.0764 | 122.5321 | 124.8441 | 123.5111 | 108.7362 | 79.8229 | 47.2603 | 19.1107 | 11.48
| Solar radiation - South | W/m2 | 43.3079 | 69.9913 | 95.889 | 111.6968 | 117.5956 | 114.5154 | 112.4582 | 121.3198 | 117.4884 | 91.766 | 48.8275 | 33.4595
| Solar radiation - West | W/m2 | 15.8737 | 32.8505 | 57.8887 | 99.5116 | 117.4067 | 129.9695 | 123.7873 | 112.1625 | 77.5864 | 44.7558 | 21.039 | 12.6101
| Solar radiation - North | W/m2 | 9.6946 | 17.9931 | 32.5862 | 47.3704 | 71.6349 | 81.0791 | 73.6048 | 57.2323 | 38.0421 | 23.1045 | 11.5625 | 7.2775
| Solar radiation - Horizontal | W/m2 | 25.0164 | 50.0401 | 95.0019 | 149.0208 | 202.0255 | 218.936 | 209.9772 | 179.9769 | 122.9641 | 68.0309 | 30.0301 | 18.016

## BE - Brussels (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| BE - Brussels |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 2.4961 | 3.2043 | 5.7071 | 8.7008 | 12.7013 | 15.504 | 17.2036 | 17.0001 | 14.3982 | 10.4012 | 6.0028 | 3.3996
| Solar radiation - East | W/m2 | 18.688 | 36.6526 | 57.3772 | 82.3341 | 113.8717 | 115.5509 | 113.1653 | 94.3485 | 70.8989 | 46.9164 | 21.6358 | 14.7062
| Solar radiation - South | W/m2 | 43.5581 | 72.3367 | 87.6165 | 102.919 | 105.9875 | 98.5648 | 101.785 | 105.3215 | 102.6728 | 89.3582 | 52.8677 | 40.4547
| Solar radiation - West | W/m2 | 17.8185 | 34.9727 | 57.2704 | 84.6219 | 110.2442 | 107.3198 | 107.1128 | 101.0103 | 68.8175 | 45.3636 | 21.1941 | 13.3778
| Solar radiation - North | W/m2 | 10.5977 | 19.6532 | 30.9592 | 47.6022 | 66.9075 | 70.2377 | 70.6362 | 57.4451 | 38.412 | 24.0498 | 12.8981 | 8.0488
| Solar radiation - Horizontal | W/m2 | 26.9997 | 54.9992 | 89.0016 | 142.0004 | 188.0014 | 196.0031 | 191.0006 | 165.9946 | 117 | 71.9963 | 33.9977 | 21.0002

## FR - Paris (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| FR - Paris |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 4.2255 | 4.6012 | 6.8343 | 9.6892 | 13.2719 | 16.2675 | 18.5734 | 18.5181 | 15.7786 | 11.7473 | 7.2303 | 4.9367
| Solar radiation - East | W/m2 | 22.2192 | 42.834 | 61.4483 | 101.5737 | 100.4768 | 122.4039 | 123.526 | 113.3737 | 82.3565 | 50.9386 | 30.446 | 18.8273
| Solar radiation - South | W/m2 | 52.6964 | 80.5729 | 98.4883 | 115.2006 | 101.9956 | 102.9306 | 112.4238 | 117.6482 | 122.8727 | 99.9328 | 75.2392 | 47.1255
| Solar radiation - West | W/m2 | 21.2168 | 38.7128 | 62.6695 | 94.1034 | 111.113 | 120.3873 | 127.8259 | 112.5762 | 85.3773 | 51.2317 | 30.8897 | 17.279
| Solar radiation - North | W/m2 | 12.2274 | 22.519 | 32.6703 | 47.0093 | 63.5962 | 76.1404 | 73.1485 | 58.6944 | 38.3839 | 26.0988 | 15.5521 | 10.1083
| Solar radiation - Horizontal | W/m2 | 32.6777 | 63.869 | 101.8156 | 158.3106 | 188.1818 | 212.4363 | 219.4381 | 187.2207 | 133.4749 | 79.8675 | 44.9576 | 26.2885

## DK - Kobenhavn (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| DK - Kobenhavn |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 1.8755 | 0.9936 | 1.9087 | 4.8729 | 9.8859 | 13.4294 | 15.0805 | 15.6216 | 13.8075 | 10.7466 | 6.6282 | 3.6667
| Solar radiation - East | W/m2 | 14.0057 | 34.3758 | 53.9755 | 105.2018 | 131.6921 | 126.0556 | 129.7021 | 114.4556 | 74.6142 | 40.177 | 19.4969 | 12.2323
| Solar radiation - South | W/m2 | 45.2767 | 83.2994 | 98.5021 | 135.5247 | 129.2167 | 120.5756 | 131.1925 | 127.2891 | 114.3765 | 84.8854 | 55.1701 | 41.8354
| Solar radiation - West | W/m2 | 15.2983 | 34.609 | 57.774 | 110.6609 | 129.2425 | 120.2404 | 134.4553 | 114.7424 | 71.4471 | 42.9839 | 19.6512 | 11.0641
| Solar radiation - North | W/m2 | 8.1705 | 15.8193 | 27.8412 | 47.7778 | 71.6809 | 76.7257 | 77.7076 | 56.0596 | 34.745 | 20.3364 | 10.1508 | 5.7799
| Solar radiation - Horizontal | W/m2 | 21.6297 | 47.1396 | 84.0289 | 159.9911 | 209.6472 | 214.2323 | 222.3454 | 176.8787 | 111.0089 | 59.7614 | 27.3711 | 14.8734

## CZ - Praha (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| CZ - Praha |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -1.1267 | 0.25164 | 3.9383 | 8.4521 | 13.3134 | 16.4356 | 17.9457 | 17.4445 | 14.0728 | 9.1859 | 3.8996 | 0.66519
| Solar radiation - East | W/m2 | 18.4379 | 35.9404 | 57.631 | 99.2994 | 115.1195 | 120.4811 | 111.1611 | 109.0412 | 77.2238 | 47.7483 | 22.299 | 12.3275
| Solar radiation - South | W/m2 | 42.3171 | 72.7038 | 92.1207 | 111.7593 | 109.4135 | 99.9668 | 100.5186 | 120.9099 | 105.4807 | 91.6764 | 49.284 | 32.7024
| Solar radiation - West | W/m2 | 16.9381 | 36.0731 | 62.1782 | 98.7924 | 121.94 | 114.2523 | 108.5741 | 111.7342 | 75.0054 | 49.4654 | 23.9722 | 13.4397
| Solar radiation - North | W/m2 | 11.1399 | 19.9876 | 33.5114 | 50.0228 | 68.9169 | 74.8248 | 69.9175 | 56.9422 | 39.6971 | 25.6739 | 13.8052 | 8.1261
| Solar radiation - Horizontal | W/m2 | 28.2796 | 55.551 | 96.4374 | 158.0394 | 199.8006 | 202.6682 | 193.6582 | 182.9533 | 121.0783 | 76.3224 | 35.2002 | 20.3039

## ES - Madrid (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| ES - Madrid |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 5.0603 | 6.5574 | 8.8577 | 11.1536 | 15.047 | 19.9369 | 23.8351 | 23.3261 | 19.8435 | 14.0505 | 8.4579 | 5.4571
| Solar radiation - East | W/m2 | 61.107 | 72.8468 | 119.9817 | 126.6543 | 157.5967 | 165.0351 | 175.5313 | 154.5161 | 136.0448 | 89.5859 | 58.3646 | 40.6709
| Solar radiation - South | W/m2 | 149.9612 | 141.331 | 176.701 | 126.7052 | 120.8158 | 112.7284 | 117.5732 | 143.6862 | 168.1998 | 159.8555 | 134.7079 | 106.7798
| Solar radiation - West | W/m2 | 59.1786 | 74.3064 | 112.9204 | 124.2967 | 153.7041 | 168.2716 | 165.5847 | 160.6347 | 127.0594 | 89.9391 | 60.2415 | 42.2569
| Solar radiation - North | W/m2 | 24.4844 | 34.0683 | 43.2191 | 58.4792 | 74.3985 | 85 | 80.4245 | 64.4818 | 47.6346 | 35.9984 | 25.858 | 21.107
| Solar radiation - Horizontal | W/m2 | 88.9542 | 115.0736 | 189.8753 | 212.0999 | 273.8497 | 309.8098 | 308.8601 | 269.8902 | 209.0177 | 141.0663 | 89.0887 | 66.0189

## PL - Warszawa (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| PL - Warszawa |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -3.3001 | -2.0984 | 1.9035 | 7.6976 | 13.5013 | 16.6968 | 18.0023 | 17.2999 | 13.1032 | 8.2012 | 3.199 | -0.90134
| Solar radiation - East | W/m2 | 16.3758 | 33.3991 | 61.6144 | 89.9479 | 120.1557 | 118.5525 | 122.6157 | 111.0611 | 67.5637 | 44.3821 | 22.147 | 10.8296
| Solar radiation - South | W/m2 | 39.6953 | 78.4673 | 97.9182 | 110.11 | 125.2655 | 108.6092 | 115.4402 | 118.2504 | 101.343 | 92.2028 | 54.5027 | 32.8543
| Solar radiation - West | W/m2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar radiation - North | W/m2 | 9.6841 | 17.9716 | 31.2967 | 48.0606 | 70.591 | 73.6759 | 75.9659 | 57.4937 | 36.8646 | 23.4573 | 11.7743 | 6.7686
| Solar radiation - Horizontal | W/m2 | 23.9987 | 52.0002 | 93.004 | 147.9969 | 210.9969 | 206.0012 | 212.9988 | 179.0005 | 111.9961 | 69.9963 | 32.0015 | 16.999

## FI - Helsinki (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| FI - Helsinki |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -4.1692 | -5.1793 | -2.6501 | 2.2547 | 8.6664 | 12.5621 | 15.1358 | 14.2685 | 10.6572 | 6.5161 | 1.7463 | -1.8738
| Solar radiation - East | W/m2 | 8.0354 | 27.8332 | 64.6797 | 104.995 | 143.2198 | 164.615 | 149.0987 | 113.2982 | 66.1192 | 28.4506 | 8.5687 | 4.2533
| Solar radiation - South | W/m2 | 26.4524 | 78.9798 | 122.0098 | 141.811 | 154.0427 | 153.9464 | 143.3778 | 131.9724 | 108.7631 | 64.5609 | 24.2458 | 14.5031
| Solar radiation - West | W/m2 | 7.6859 | 29.139 | 64.3466 | 104.5679 | 141.9239 | 155.9522 | 140.4663 | 105.0586 | 72.0999 | 32.8334 | 10.1682 | 4.2809
| Solar radiation - North | W/m2 | 4.3873 | 12.9336 | 26.2605 | 44.2033 | 74.4411 | 91.7639 | 80.5354 | 54.4508 | 31.5799 | 16.1264 | 5.402 | 2.7782
| Solar radiation - Horizontal | W/m2 | 10.5768 | 36.727 | 86.6872 | 149.2153 | 219.8137 | 252.6373 | 226.9896 | 168.1862 | 96.3438 | 43.7123 | 12.8449 | 6.1059

## IT - Rome (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| IT - Rome |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 6.2 | 7.1 | 9.7 | 12.3 | 16.5 | 20.6 | 23.7 | 23.3 | 19.6 | 15.4 | 11.5 | 7.6
| Solar radiation - East | W/m2 | 55 | 68.6111 | 102.2222 | 134.1667 | 150.8333 | 166.1111 | 168.0556 | 153.3333 | 128.8889 | 92.5 | 62.7778 | 45
| Solar radiation - South | W/m2 | 126.3889 | 140.5556 | 151.1111 | 140.5556 | 125.8333 | 115.8333 | 124.4444 | 139.7222 | 163.6111 | 173.6111 | 133.8889 | 121.9444
| Solar radiation - West | W/m2 | 55.8333 | 72.7778 | 107.5 | 131.9444 | 156.6667 | 162.2222 | 178.0556 | 157.5 | 130.5556 | 98.0556 | 55 | 47.7778
| Solar radiation - North | W/m2 | 27.2222 | 33.6111 | 46.3889 | 61.3889 | 80.5556 | 91.3889 | 89.4444 | 66.3889 | 53.0556 | 37.7778 | 26.6667 | 21.3889
| Solar radiation - Horizontal | W/m2 | 76.1111 | 108.0556 | 160 | 213.8889 | 258.0556 | 281.1111 | 290 | 251.9444 | 198.8889 | 138.8889 | 85 | 65

## NO - Oslo (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| NO - Oslo |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -4.3016 | -3.9993 | -0.19879 | 4.5022 | 10.7992 | 15.2004 | 16.4001 | 15.1989 | 10.7985 | 6.2995 | 0.70014 | -3.1013
| Solar radiation - East | W/m2 | 11.2881 | 31.1599 | 59.2186 | 100.0694 | 150.9789 | 136.1157 | 136.0036 | 116.7208 | 76.2604 | 37.3667 | 16.0559 | 8.8243
| Solar radiation - South | W/m2 | 40.3457 | 94.9235 | 120.2046 | 139.3546 | 157.929 | 137.5694 | 142.1405 | 141.1809 | 121.2975 | 76.4359 | 56.1632 | 40.0482
| Solar radiation - West | W/m2 | 11.5457 | 35.1761 | 67.7438 | 100.4958 | 152.6829 | 145.3831 | 147.9331 | 112.1543 | 76.1856 | 32.1658 | 15.8349 | 8.3296
| Solar radiation - North | W/m2 | 5.5007 | 13.2846 | 27.2614 | 44.0779 | 77.3215 | 88.5282 | 81.4587 | 56.2384 | 32.1289 | 16.7925 | 7.2994 | 3.9203
| Solar radiation - Horizontal | W/m2 | 13.9826 | 40.4894 | 87.5411 | 145.7384 | 228.433 | 228.9128 | 223.9505 | 172.2465 | 106.0216 | 48.1131 | 20.2033 | 9.7484

## RO - Bucharest (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| RO - Bucharest |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -2.4009 | -0.09747 | 4.823 | 11.2974 | 16.7027 | 20.199 | 22.0003 | 21.1993 | 16.9011 | 10.7988 | 5.1957 | 0.20349
| Solar radiation - East | W/m2 | 36.2089 | 51.5873 | 71.3896 | 112.5802 | 127.8681 | 152.9977 | 150.5776 | 132.1685 | 106.9653 | 71.5965 | 37.0868 | 24.0763
| Solar radiation - South | W/m2 | 91.3127 | 99.294 | 108.0813 | 121.272 | 113.9456 | 114.387 | 118.7302 | 139.4228 | 144.1998 | 129.9242 | 84.0938 | 59.2753
| Solar radiation - West | W/m2 | 40.0989 | 51.7398 | 70.7172 | 108.5347 | 127.8636 | 146.2554 | 149.3134 | 144.123 | 107.6208 | 70.146 | 37.6586 | 25.0146
| Solar radiation - North | W/m2 | 18.1138 | 26.4542 | 36.3616 | 50.5201 | 73.1082 | 83.816 | 76.822 | 62.4541 | 44.6485 | 33.6865 | 19.6802 | 13.6036
| Solar radiation - Horizontal | W/m2 | 55.003 | 82.0019 | 119.0035 | 184.9992 | 224.9993 | 266.995 | 263.0052 | 236.001 | 170.0004 | 112.9999 | 58.0008 | 37.9973

## HU - Budapest (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| HU - Budapest |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -0.49879 | 2.0052 | 6.3996 | 11.8007 | 16.5962 | 19.7015 | 21.5013 | 20.8995 | 16.8985 | 11.5027 | 5.6989 | 1.5008
| Solar radiation - East | W/m2 | 25.5925 | 46.0987 | 72.3611 | 103.4414 | 124.2425 | 132.0251 | 137.6355 | 127.3454 | 95.3816 | 61.2612 | 31.211 | 20.6866
| Solar radiation - South | W/m2 | 68.1653 | 86.0049 | 109.9757 | 121.3171 | 118.0346 | 113.6759 | 120.2449 | 130.2322 | 134.8673 | 115.3636 | 75.5336 | 58.1765
| Solar radiation - West | W/m2 | 26.1201 | 45.8631 | 72.6561 | 107.2589 | 125.7736 | 132.5752 | 139.2331 | 121.5487 | 95.3349 | 59.5949 | 33.3098 | 20.7355
| Solar radiation - North | W/m2 | 13.8702 | 23.2949 | 36.4479 | 52.4055 | 72.0158 | 79.838 | 75.5511 | 60.2584 | 43.196 | 29.7036 | 17.353 | 11.0652
| Solar radiation - Horizontal | W/m2 | 40.096 | 69.134 | 116.1126 | 177.0814 | 218.0892 | 239.1512 | 246.1544 | 207.08 | 152.1427 | 95.1564 | 49.1154 | 31.0689

## IE - Dublin (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| IE - Dublin |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 5.0996 | 5.0021 | 6.2052 | 7.8015 | 10.3995 | 13.3 | 15.0009 | 14.702 | 13.0008 | 10.6013 | 7.0965 | 6.0004
| Solar radiation - East | W/m2 | 20.1169 | 29.4461 | 61.7899 | 92.473 | 117.9398 | 117.6721 | 113.5275 | 89.9996 | 72.8947 | 42.4003 | 22.049 | 14.6069
| Solar radiation - South | W/m2 | 62.1132 | 69.0819 | 102.9607 | 116.6782 | 117.3622 | 106.4117 | 111.07 | 102.5967 | 111.7612 | 87.1397 | 64.0293 | 40.7747
| Solar radiation - West | W/m2 | 19.3526 | 34.1654 | 60.8968 | 93.588 | 113.4117 | 109.3696 | 123.8766 | 95.4099 | 75.6501 | 43.9901 | 21.8708 | 12.7371
| Solar radiation - North | W/m2 | 9.5557 | 17.1135 | 30.4962 | 44.9826 | 64.655 | 74.3615 | 72.5825 | 53.0791 | 35.5278 | 22.9267 | 11.1485 | 7.5422
| Solar radiation - Horizontal | W/m2 | 27.0001 | 48.0006 | 93.9987 | 150 | 193.0007 | 200.0004 | 200.0019 | 153.0022 | 115.0031 | 66.0006 | 31.9981 | 19.0013

## GB - London (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| GB - London |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | 4.9991 | 5.0018 | 7.2067 | 8.9026 | 12.1978 | 15.6004 | 17.7984 | 17.8031 | 15.0036 | 11.0972 | 7.7935 | 6.1009
| Solar radiation - East | W/m2 | 18.2844 | 30.5527 | 56.4385 | 80.9336 | 108.1795 | 112.9877 | 110.9808 | 96.9071 | 78.0733 | 42.7808 | 26.463 | 12.3417
| Solar radiation - South | W/m2 | 41.5752 | 60.1811 | 85.5208 | 98.4969 | 100.7086 | 101.4506 | 99.7155 | 104.9918 | 103.8434 | 81.228 | 58.2442 | 34.0028
| Solar radiation - West | W/m2 | 18.2844 | 30.5527 | 56.4385 | 80.9336 | 108.1795 | 112.9877 | 110.9808 | 96.9071 | 78.0733 | 42.7808 | 26.463 | 12.3417
| Solar radiation - North | W/m2 | 10.3905 | 17.8551 | 31.0032 | 44.6763 | 64.7237 | 74.9402 | 69.6588 | 50.5096 | 37.8245 | 23.9904 | 13.0486 | 8.1582
| Solar radiation - Horizontal | W/m2 | 25.9976 | 47.0015 | 89.0001 | 136.9973 | 179.0016 | 198.0004 | 185.9991 | 160.9991 | 116.9965 | 67.9962 | 34.9977 | 19.9996

## LT - Vilnius (hidden)
This sheet contains predefined monthly climate data. If you want to define your own monthly climate data file use the sheets Climate 1, 2 and 3.
| LT - Vilnius |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Outdoor temperature | °C | -5.9044 | -4.7259 | -0.60336 | 5.8164 | 12.548 | 15.8594 | 16.9741 | 16.3378 | 11.7169 | 6.7708 | 1.4539 | -2.8098
| Solar radiation - East | W/m2 | 16.2829 | 40.8139 | 63.4618 | 94.9329 | 131.0842 | 135.3897 | 136.1526 | 110.9558 | 65.1852 | 43.5521 | 16.7103 | 9.8928
| Solar radiation - South | W/m2 | 46.1302 | 93.3441 | 106.7354 | 126.0995 | 136.8354 | 118.9896 | 125.983 | 127.6307 | 96.4159 | 88.9038 | 45.6902 | 29.0087
| Solar radiation - West | W/m2 | 15.4764 | 37.3603 | 62.2629 | 105.0853 | 133.7459 | 125.8283 | 127.2319 | 117.1722 | 66.6366 | 43.5484 | 19.0073 | 9.571
| Solar radiation - North | W/m2 | 8.8971 | 18.0969 | 30.6519 | 47.1165 | 71.9318 | 80.2076 | 76.0588 | 56.1585 | 34.5988 | 20.2345 | 10.0154 | 5.8583
| Solar radiation - Horizontal | W/m2 | 23.1944 | 53.7698 | 95.8927 | 152.875 | 218.2385 | 220.1327 | 218.1 | 177.3395 | 106.0293 | 61.3504 | 26.2388 | 14.07

## CSI reference heating (hidden)
This sheet contains the calculation of the reference for the Climate Severity Index for heating (based on climate: BE - Brussels)
Don't change anything in this sheet!
Calculation energy use climate severity index heating (QCSI,H)
Climate severity index variables
| qsol, average | W/m2 | 22.6656 | 40.9038 | 58.3058 | 79.3693 | 99.2527 | 97.9183 | 98.1748 | 89.5313 | 70.2003 | 51.422 | 27.1489 | 19.1469
| aH | - | 217.4805 | 221.0216 | 233.5356 | 248.5042 | 268.5067 | 282.5201 | 291.0181 | 290.0007 | 276.991 | 257.006 | 235.0139 | 221.998
| bH | - | 11.5467 | 11.1819 | 10.8339 | 10.4126 | 10.0149 | 10.0416 | 10.0365 | 10.2094 | 10.596 | 10.9716 | 11.457 | 11.6171
| cH | - | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| QCSI,H | W | 2527.5637 | 2233.8038 | 1672.6818 | 932.9439 | 0 | 0 | 0 | 0 | 0 | 845.7613 | 1943.482 | 2440.8276
Energy use climate severity index heating (QCSI,H)
| QCSI,H | W | 12597.0641

## CSI reference cooling (hidden)
This sheet contains the calculation of the reference for the Climate Severity Index for cooling (based on climate: BE - Brussels)
Don't change anything in this sheet!
Calculation energy use climate severity index cooling (QCSI,C)
Climate severity index variables
| qsol, average | W/m2 | 22.6656 | 40.9038 | 58.3058 | 79.3693 | 99.2527 | 97.9183 | 98.1748 | 89.5313 | 70.2003 | 51.422 | 27.1489 | 19.1469
| aC | - | 192.4805 | 196.0216 | 208.5356 | 223.5042 | 243.5067 | 257.5201 | 266.0181 | 265.0007 | 251.991 | 232.006 | 210.0139 | 196.998
| bC | - | 11.5467 | 11.1819 | 10.8339 | 10.4126 | 10.0149 | 10.0416 | 10.0365 | 10.2094 | 10.596 | 10.9716 | 11.457 | 11.6171
| cC | - | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| QCSI,C | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy use climate severity index cooling (QCSI,C)
| QCSI,C | W | 0